## SOR
TENDER DOCUMENT FOR MECHANICAL AND ELECTRICAL WORKS FOR CONSTRUCTION OF CNG DAUGHTER BOOSTER STATIONS IN EAST & WEST GODAVARI GEOGRAPHICAL AREAS Tender No.: 05/51/E/0086/GGPL/001-iv SCHEDULE OF RATES
Name of the Bidder
Item | Activity | Unit | Quantity | Unit Rate inclusive of all applicable taxes, duties & other levies [if any] payable by the Contractor under the Contract, or for any other cause except final GST (In INR) (In figures) | Unit Rate inclusive of all applicable taxes, duties & other levies [if any] payable by the Contractor under the Contract, or for any other cause except final GST (In INR) (In Words) | Amount inclusive of all applicable taxes & duties & other levies [if any] payable by the Contractor under the Contract, or for any other cause except final GST (In INR)
I | II | III | IV | V |  | VI = IV x V
1 | SECTION-A : SS TUBE & FITTING - SUPPLY, LAYING & TESTING
2 | Laying, testing and commissioning of SS tubes along with fittings as per Technical Specification, Typical P & ID for type of CNG station and scope of work including handling, lifting, transportation from stores to CNG stations.
3 | ¾”OD X 0.095” min Wall thk. SS Tube (Refer TS Section III - A) | RM | 1500
4 | ½”OD X 0.083” min Wall thk. SS Tube (Refer TS Section III - A) | RM | 60
5 | Supply of SS Fittings,Valves
6 | Quick Connect Body & Stem
7 | End connection:½" Tube OD, for stem & ½”NPT (F) for body Material : SS316; Rated pressure : 5000 PSI @ 70°F Temperature: 0°F to 400°F | Nos. | 12
8 | Plug
9 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6
10 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
11 | Caps
12 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6
13 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
14 | Union
15 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 350
16 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
17 | Reducing Union
18 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 36
19 | Equal Tee
20 | Size:½” OD x ½” OD x ½” OD, Material:SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 5
21 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 ( Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
22 | Reducing Union Tee
23 | ¾" OD x ½" OD x ¾" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 18
24 | Tube End Connection
25 | ½” Tube End & ¾” OD with Ferrule Fitting, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
26 | Nut
27 | ¾ " OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
28 | ½" OD, Material : SS316(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6
29 | Front Ferrule
30 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
31 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6
32 | Back Ferrule
33 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
34 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6
35 | Male Connector
36 | Size ¼” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
37 | Size 1/2” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12
38 | Cross
39 | 3/4" OD X 3/4” X 3/4" OD X3/4" OD Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 3
40 | SS Ball Valves, conforming to MECON’s Technical Specification No. MEC/TS/05/62/048 for SS Ball Valves of following sizes, specifications as indicated below :
41 | 2-Way Trunnion/Floating Full Bore Ball Valve ¾" | Nos. | 150
42 | 2-Way Trunnion/Floating Full Bore Ball Valve ½" | Nos. | 12
43 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection | Nos. | 12
44 | Conductive Core Thermoplastic Hose
45 | 3/8” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling | Nos. | 12
46 | Supply of SS 304 Tubes along with isolation valves, reducers & fittings etc.as per Technical Specification, Typical schematic drg. for Ins. air line of CNG station and scope of work including handling, storage,lifting, transportation upto CNG stations. (Note:Total no.of ferrule fittings may be considered as one jointing ferrule at every 5.0 m)
47 | 1/4”OD X 0.035” min Wall thk. SS Tube (Refer TS Section III - A) | RM | 30
48 | Laying, testing and commissioning of SS 304 Tubes along with isolation valves, reducers & fittings etc.as per Technical Specification, Typical schematic drg. for Ins. air line of CNG station and scope of work including handling, storage,lifting, transportation upto CNG stations. (Note:Total no.of ferrule fittings may be considered as one jointing ferrule at every 5.0 m)
49 | 1/4”OD X 0.035” min Wall thk. SS Tube (Refer TS Section III - A) | RM | 30
50 | SECTION-B : ERECTION OF MECH. EQUIPMENT
51 | Handling (including lifting and transportation from Client's store within city to CNG stations) and erecting in position, the following equipment either on the foundation at Ground level or on roof at 3.5 m above ground level. Contractor's scope shall include supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, etc. :
52 | Cascade 4500/3000/2200 L water capacity. Erection at + 4.0 M level (Refer TS Section III - B) | Nos. | 12
53 | Cascade 4500/3000/2200 L water capacity, Erection at + Ground level (Refer TS Section III - B) | Nos. | 2
54 | Dispenser Erection at + Ground Level | Nos. | 12
55 | Note: The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may increase or decrease at site at the time of actual execution and as per the discretion of Owner/ Engineer-in-charge. The unit rate shall be operated to work out the final payment due to Contractor.
56 | SECTION-C : SUPPLY, ERECTION & COMMISSIONING OF MISCELLANEOUS ITEM
57 | Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC
58 | Air compressor pump (Refer TS Section III - C) (Tyre Inflator) | No. | 1
59 | Water cooler (Refer TS Section III - C) | No. | 1
60 | STRUCTURAL WORKS
61 | Supply, fabrication & erection of Steel structure
62 | Supplying, Fabricating & Erecting in position steel structures fabricated from MS rolled section conforming to IS:2062 and/or from pipes conforming to IS:1161 for cascade supporting structures, loading/unloading platform, MS Gratings, Cat Ladder, handrails, hoardings for signages, LCV stand,Sprial Stair case, etc. or any other structures required as per constructon drawings for completion of works, including surface preparation by mechanical cleaning including application of one coat of Zinc phosphate primer of DFT 35 microns at shop, second coat of Zinc phosphate primer of DFT 35 microns at site after erection and two coats of finishing paint of synthetic enamel of DFT 25 microns each per coat at site, including loading, transportation and unloading delivery at erection site of all fabricated structures, storage and handling at site, site assembly and finally erection of structures at appropriate location, alignment and welding of all structures true to line, level, plumb and dimension. The work shall be completed in all respect as per drawings, technical specification and direction of the Engineer-in-Charge. | M.Ton. | 1
63 | PRESSURE GAUGES
64 | Supply, installation and calibration of pressure Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG. | Nos. | 12
65 | TEMPERATURE GAUGES
66 | Supply, installation and calibration of Temperature Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG. | Nos. | 12
67 | TESTING & COMMISSIONING OF ALREADY LAID SS TUBES
68 | Testing & Commissioning of the existing SS tubing of various size from 1/4" to 3/4" sizes including fixing of any damaged/missing fittings/accessories such as valves, unions, Ferrules, Tee, caps etc. as required. Item includes Carrying out pneumatic testing as per approved procedures; providing all tools, tackles, instruments, manpower and other related accessories for carrying out the testing of tubes. The item is only for the tesing & commissioning. Payment against supply of any damaged/missing fitting shall be made as per the relevant Items mentioned elsewhere in the SOR. | RM | 1000
69 | Installation of Mass Flow Meter
70 | Installation of Owner-Supplied Mass Flow Meter to measure the gas unloaded from LCV/HCV. The item includes mounting of the mass flow meter on SS tubing, cutting and bending of SS tubing, installation of SS tube fittings (double ferrule type), reducers/adaptors/connectors/unions as required, alignment of the flow meter, leak testing with nitrogen as per the Engineer-in-Charge's instructions. | Nos. | 12
71 | ELECTRICAL WORKS (SUPPLY)
72 | SUPPLY
73 | Design, engineering, manufacture, shop testing, supply including packing and forwarding, transportation, delivery at storage and from storage to site of power distribution board (PDB) :
74 | 415 V, 36 KA single front type indoor PDB for Daughter Booster Station to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no. MEC/23V2/05/E9/E/1081C & as per standard Specification. Single In-comer of 125 Amp(with Single phase preventer ) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) along with VMR. Outgoing with 01 no. 80 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Booster Compressor. Outgoing with 02 nos. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for APFC panel. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C, S/C & E/F RELASE) for UPS and Static Bypass. Outgoing with 3 no. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 no. 40A Fuse and 3 nos. 10A DP MCB without Timer | Nos. | 12
75 | Floor mounted APFC Panel of 10KVAR capacitor bank in steps of 4x2.5 KVAR capacitors consisting of bus bar chamber, cable alley incoming (MCCB), outgoing feeder (MCBs) as specified in tender specification. | Nos. | 12
76 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 125A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5CX120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with On, Off, Trip, RYB Indication, Voltmeter & Ammeter etc. | Nos. | 12
77 | Design, engineering,supply including packing and forwarding, transportation, delivery at storage, of the complete earthing and lightning protection system, earth electrodes/ pit, earth main ring, earthing of electrical equipments, instrument panels, field instruments, process equipments and pipes/ flanges including all associated civil work with all material (Like Bitumen coating) and labour as per specification and drawings approved by the company in with IS 3043. |  | 0
78 | Earth Pits- GI PIPE Electrode with 6 mm thick chequered plate cover | Nos. | 72
79 | Earth Pits- Copper plate Electrode with 6 mm thick chequered plate cover | Nos. | 24
80 | GI Strip (50X6) mm | Mtrs. | 1800
81 | GI Strip (25X3) mm | Mtrs. | 3000
82 | GI lightning rod 25 mm dia. 1800 mm long including supply of all hardware bare copper rope labour etc. complete as per approved drawings, specifications and directions of Engineer-In-Charge. | Nos. | 2
83 | Arrangement for Earthing of LCV with Flexible green Cu wire (10 sqmm of 30 Meter length) ,Crocodile Clamps (including bolting arrangement), Flexible PVC and other item etc. | Set | 12
84 | Design, engineering,supply including packing and forwarding, transportation, delivery at storage, of the 1.1kV grade XLPE insulated, PVC sheathed, FRLS power and control cables (conforming to IS:7098 and specification) of following sizes in trenches/ excavated under ground trench /trays, pulling through pipes and its proper sealing, cutting of paved area, roads etc. |  | 0
85 | 3.5x 95 mm2 A2XFY | Mtrs | 1200
86 | 3.5x 50 mm2 A2XFY | Mtrs | 1800
87 | 4x 6 mm2 2XWY | Mtrs | 600
88 | 4x 2.5 mm2 2XWY | Mtrs | 9000
89 | Supply including packing and forwarding, transportation, delivery at storage of lighting fixtures complete with mounting bracket, flame proof/non flame proof, control gear box as per the type of fixture, lamps etc. including civil work with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects. |  | 0
90 | Street lighting, integral flame proof well glass fixture (CMIFR approved for Zone-1/2 gas group IIA & IIB) with 72 W LED luminaire with flame proof control gear Model no. FLPW-1095 of Baliga make or equivalent) | Nos. | 96
91 | Supply of the underlights for the canopy as specified including lighting fixture flame proof enclosure for Bulk Head Fitting( BH/OA/124, 1 x LED, 150W)of Sudhir make or equivalent, juction boxes etc. as requried. | Nos. | 4
92 | Street lighting pole 6mtr high GI octagonal pole (Type BOP-6030 of Bajaj make or equivalent) complete with bracket, GI clamps for fixing flame proof control gear box as per standard drawing (MEC/SD/05/E9/77/04) & specification (MEC/TS/05/E9/077B). | Nos. | 96
93 | UPS SYSTEM |  | 0
94 | Design, supply, packing, forwarding, delivery by equipment supplier at site including commissioning spares as required of UPS systems as per specification, block diagram and following rating : |  | 0
95 | 2KVA, 230 V Single phase, 50 Hz, single industrial type, UPS system suitable for input Power supply voltage of 320V-460V-TPN with healthy single-Phase Selection, Output 230V +/-1%, AC with Bypass supply, Battery Bank, ACDB (Incomer 32A DP MCB & Outgoing 10 Nos. 6A to 10A DP MCB) and 8.0 hrs. Battery backup (VRLA, 12V) and battery capacity shall not be less than 22.0 KVAh (where KVAH = battery AH x 12 V x No. of Batteries). As per enclosed Specification, Block diagram & Data sheet and shall be complete in all respect. Including All interconnecting cables among UPS, Rectifier, battery stand, ACDB etc (30 mtr shall be considered between battery bank and UPS panel, 30 mtr cable shall be considered between ACDB and UPS panel. | Nos. | 12
96 | Supply of following sizes of GI With Class B (Medium Duty, For straight route length) / HDPE Pipe (for bend route) in required length, supply of clamps, small iron structures, spacers plugs, sealent etc. and materials complete as per approved drawings and directions of Engineer-In-Charge. |  | 0
97 | 50 mm NB | Mtrs | 6000
98 | 100 mm NB | Mtrs | 3600
99 | Supply of following Hot Dip Galvanized Ladder/Perforated Type cable trays (as per IS 2629) including bends, tee, crosses,horizontal and vertical splices along with cable tray cover(Wherever required for Asthetic look ) etc. as required including supply of all G.I hardwares, all labour and material as required as per standard drawings, specification and direction of Engineer-in-charge |  | 0
100 | Perforated type, made from 50mm height and 2.5 mm thick sheet steel & galvanized (86 microns) of following sizes. |  | 0
101 | 150mm wide | Mtrs | 120
102 | 300mm wide | Mtrs | 120
103 | Erection Material |  | 0
104 | Supply of MS base frame support for switch gear and bracket for misc. electrical equipment,cable tray support out of roled MS section,pipes,plates etc including welding, bolting, reveting, supply of necessary anchor bolts and grouting etc supply of paints applying one coat of anti rust primer two finish coats of approved synthetic enamel paints including bracking walls, floors etc for structure as required including supply of all GI hardware materials including all labour and materials complete as required and the direction of Engineer-in-charge. |  | 0
105 | For Daughter Booster Station | L/S | 12
106 | Supply of the following including the supply of necessary clamp, bolts, rawl plugs etc. breaking and making good of walls, if required , and including all labour and materials complete as per directions of Engineer-In-Charge, applicable standards and Indian Electricity rules. |  | 0
107 | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark , Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate | Nos. | 12
108 | Caution boards (Danger, High Volatage) including supply of necessary clamps, bolts and other hardware. | Nos. | 24
109 | Single Line Diagram complete in glass frame. | Nos. | 12
110 | Supply of Insulating Mats 11kV grade (as per IS:15652 - 2006) of 1000mm width, required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per applicable Indian or International standards and Indian Electricity Rules. | Mtrs | 60
111 | Supply of electrical accessories including, cable tags, cable tie ,Flexible pvc conduit,cable marker, nickle plated lugs, double compressed brass cable glands,brass adaptar/reducers/nipples, fixing of metallic anchor fasteners for supporting of cable trays and misc. electrical switchgear including all labour and materials complete as required and as per directions of Engineer-In-Charge. |  | 0
112 | For Daughter Booster Station | L/S | 12
113 | Supply of required materials for Construction of Cable pit with pit cover (SFRC cover HD-20 of IS-12592) including civil works repair, concrete wall/brick wall & its materials, cable conduits interface & its water sealing, cable support structure including all labour and materials complete in all aspect as per approved drawings and directions of Engineer-In-Charge. |  | 0
114 | 500X500(of inside clearance)X 600(Depth) | Nos. | 96
115 | 750X750(of inside clearance)X800(Depth) | Nos. | 48
116 | Servo Volatge Stablizer
117 | Supply of 50 kVA oil-cooled Servo Voltage Stabilizer, suitable for outdoor duty with IP-55 metallic enclosure (IP-66 for control switchgear), complete with suitable rated incomer MCCB, input voltage range 320 V to 480 V, output voltage 415 V ±1%, outgoing MCCB, two (2) Nos. 125 A, AC-23 duty Changeover Switches (COS), complete in all respects. The Stabilizer shall be installed outdoors under a structural weatherproof shed over a plinth to protect it from rain and dust. The successful bidder shall submit all drawings for Stabilizer mounting along with the shed. All cable terminations, including supply of cable glands, lugs and other termination accessories, shall be in the bidder's scope. | Nos. | 12
118 | ELECTRICAL WORKS (ERECTION)
119 | ERECTION, TESTING AND COMMISSIONING
120 | Erection, Testing and Commissioning of power distribution board (PDB) and Lighting Distribution Board (LDB) :
121 | 415 V, 36 KA single front type indoor PDB for Daughter Booster Station to receive input power consisting of bus bar chamber, cable alley,outgoing with Fuse complete with wiring, indication lamp, ammeter, voltmeter, MFM (Multi Function Meter) etc including all labour and materials with operating mechanism, all accessories, mandatory spares as per data sheet, auxiliaries with FLP LCS(Local Control switch) for tripping the main incomer of PDB etc complete in all respects as specified in technical specification, data sheet & SLD no.MEC/E0086/05/E1/E/1081A & as per standard Specification. Single In-comer of 125 Amp (with Single phase preventer ) 4P MCCB (with Micro processor and based O/C,S/C & E/F RELASE with LSIG & Shunt trip) along with VMR. Outgoing with 01 no. 80 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for Booster Compressor. Outgoing with 02 nos. 63 Amp TPN MCCB (with TM based O/C,S/C & E/F RELASE) for APFC panel. Outgoing with 02 nos. 32 Amp TPN MCCB (with TM based O/C, S/C & E/F RELASE) for UPS and Static Bypass. Outgoing with 3 no. 40A Fuse and 3 nos. 10A DP MCB with Timer(24Hrs) Auto/Mannual Outgoing with 3 no. 40A Fuse and 3 nos. 10A DP MCB without Timer | Nos. | 12
122 | Floor mounted APFC Panel of 10KVAR capacitor bank in steps of 4x2.5 KVAR capacitors consisting of bus bar chamber, cable alley incoming (MCCB), outgoing feeder (MCBs) as specified in tender specification. | Nos. | 12
123 | Outdoor type dust & weather proof sheet steel (2 mm thick) enclosed MCCB of following rating for mounting on wall or pedestal. 125A, 415V, 4 Pole AC-23 duty and suitable for termination of 3.5CX120/95/50 sq.mm A2XFY cable on incomer terminals and outgoing terminals with On, Off, Trip, RYB Indication, Voltmeter & Ammeter etc. | Nos. | 12
124 | Erection, Testing and Commissioning of the complete earthing and lightning protection system, earth electrodes/ pit, earth main ring, earthing of electrical equipments, instrument panels, field instruments, process equipments and pipes/ flanges including all associated civil work with all material (Like Bitumen coating) and labour as per specification and drawings approved by the company in with IS 3043. |  | 0
125 | Earth Pits- GI PIPE Electrode with 6 mm thick chequered plate cover | Nos. | 72
126 | Earth Pits- Copper plate Electrode with 6 mm thick chequered plate cover | Nos. | 24
127 | GI Strip (50X6) mm | Mtrs. | 1800
128 | GI Strip (25X3) mm | Mtrs. | 3000
129 | GI lightning rod 25 mm dia. 1800 mm long including supply of all hardware bare copper rope labour etc. complete as per approved drawings, specifications and directions of Engineer-In-Charge. | Nos. | 2
130 | Arrangement for Earthing of LCV with Flexible green Cu wire (10 sqmm of 30 Meter length) ,Crocodile Clamps (including bolting arrangement), Flexible PVC and other item etc. | Set | 12
131 | Laying, termination,glanding, testing of the 1.1kV grade XLPE insulated, PVC sheathed, FRLS power and control cables (conforming to IS:7098 and specification) of following sizes in trenches/ excavated under ground trench /trays, pulling through pipes and its proper sealing, cutting of paved area, roads etc. |  | 0
132 | 3.5x 95 mm2 A2XFY | Mtrs | 1200
133 | 3.5x 50 mm2 A2XFY | Mtrs | 1800
134 | 4x 6 mm2 2XWY | Mtrs | 600
135 | 4x 2.5 mm2 2XWY | Mtrs | 9000
136 | Erection, Testing and Commissioning of lighting fixtures,Pole complete with mounting bracket, flame proof/non flame proof, control gear box as per the type of fixture, lamps etc. including civil work with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects. |  | 0
137 | Street lighting, integral flame proof well glass fixture (CMIFR approved for Zone-1/2 gas group IIA & IIB) with 72 W LED luminaire with flame proof control gear Model no. FLPW-1095 of Baliga make or equivalent) | Nos. | 96
138 | Erection of the underlights for the canopy as specified including lighting fixture flame proof enclosure for Bulk Head Fitting( BH/OA/124, 1 x LED, 150W)of Sudhir make or equivalent, juction boxes etc. as requried. | Nos. | 4
139 | Street lighting pole 6mtr high GI octagonal pole (Type BOP-6030 of Bajaj make or equivalent) complete with bracket, GI clamps for fixing flame proof control gear box as per standard drawing (MEC/SD/05/E9/77/04) & specification (MEC/TS/05/E9/077B). | Nos. | 96
140 | UPS SYSTEM |  | 0
141 | Erection, Testing and Commissioning by equipment manufacturer at site including commissioning spares as required of UPS systems as per specification, block diagram and following rating : |  | 0
142 | 2KVA, 230 V Single phase, 50 Hz, single industrial type, UPS system suitable for input Power supply voltage of 320V-460V-TPN with healthy single-Phase Selection, Output 230V +/-1%, AC with Bypass supply, Battery Bank, ACDB (Incomer 32A DP MCB & Outgoing 10 Nos. 6A to 10A DP MCB) and 8.0 hrs. Battery backup (VRLA, 12V) and battery capacity shall not be less than 22.0 KVAh (where KVAH = battery AH x 12 V x No. of Batteries/1000). As per enclosed Specification, Block diagram & Data sheet and shall be complete in all respect. Including All interconnecting cables among UPS, Rectifier, battery stand, ACDB etc (30 mtr shall be considered between battery bank and UPS panel, 30 mtr cable shall be considered between ACDB and UPS panel. | Nos. | 12
143 | Erection of following sizes of GI With Class B (Medium Duty, For straight route length) / HDPE Pipe (for bend route) in required length ,supply of clamps, small iron structures, spacers plugs, sealent etc. and materials complete as per approved drawings and directions of Engineer-In-Charge. |  | 0
144 | 50 mm NB | Mtrs | 6000
145 | 100 mm NB | Mtrs | 3600
146 | Erection, Testing and Commissioning of following Hot Dip Galvanized Ladder/Perforated Type cable trays (as per IS 2629) including bends, tee, crosses,horizontal and vertical splices along with cable tray cover (Wherever required for Asthetic look ) etc. as required including supply of all G.I hardwares, all labour and material as required as per standard drawings, specification and direction of Engineer-in-charge. |  | 0
147 | Perforated type, made from 50mm height and 2.5 mm thick sheet steel & galvanized (86 microns) of following sizes. |  | 0
148 | 150mm wide | Mtrs | 120
149 | 300mm wide | Mtrs | 120
150 | Erection Material |  | 0
151 | Erection, Fixing and Commissioning of MS base frame support for switch gear and bracket for misc. electrical equipment,cable tray support out of roled MS section,pipes,plates etc including welding, bolting, reveting, supply of necessary anchor bolts and grouting etc supply of paints applying one coat of anti rust primer two finish coats of approved synthetic enamel paints including bracking walls, floors etc for structure as required including supply of all GI hardware materials including all labour and materials complete as required and the direction of Engineer-in-charge. |  | 0
152 | For Daughter Booster Station | L/S | 12
153 | Erection and Commissioning of the following including necessary clamp, bolts, rawl plugs etc. breaking and making good of walls, if required , and including all labour and materials complete as per directions of Engineer-In-Charge, applicable standards and Indian Electricity rules. |  | 0
154 | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark , Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate | Nos. | 12
155 | Caution boards (Danger, High Volatage) including supply of necessary clamps, bolts and other hardware. | Nos. | 24
156 | Single Line Diagram complete in glass frame. | Nos. | 12
157 | Laying and pasting of Insulating Mats 11kV grade (as per IS:15652 - 2006) of 1000mm width, required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per applicable Indian or International standards and Indian Electricity Rules. | Mtrs | 60
158 | Erection, Commissioning and fixing of electrical accessories including, cable tags, cable tie ,Flexible pvc conduit,cable marker, nickle plated lugs, double compressed brass cable glands,brass adaptar/reducers/nipples, fixing of metallic anchor fasteners for supporting of cable trays and misc. electrical switchgear including all labour and materials complete as required and as per directions of Engineer-In-Charge. |  | 0
159 | For Daughter Booster Station | L/S | 12
160 | Construction of Cable pit with pit cover (SFRC cover HD-20 of IS-12592) including civil works repair, concrete wall/brick wall & its materials, cable conduits interface & its water sealing, cable support structure including all labour and materials complete in all aspect as per approved drawings and directions of Engineer-In-Charge. |  | 0
161 | 500X500(of inside clearance)X 600(Depth) | Nos. | 96
162 | 750X750(of inside clearance)X800(Depth) | Nos. | 48
163 | Servo Volatge Stablizer
164 | Erection, Testing and Commissioning of 50 kVA oil-cooled Servo Voltage Stabilizer, suitable for outdoor duty with IP-55 metallic enclosure (IP-66 for control switchgear), complete with suitable rated incomer MCCB, input voltage range 320 V to 480 V, output voltage 415 V ±1%, outgoing MCCB, two (2) Nos. 125 A, AC-23 duty Changeover Switches (COS), complete in all respects. The Stabilizer shall be installed outdoors under a structural weatherproof shed over a plinth to protect it from rain and dust. The successful bidder shall submit all drawings for Stabilizer mounting along with the shed. All cable terminations, including supply of cable glands, lugs and other termination accessories, shall be in the bidder's scope. | Nos. | 12
165 | All works relating to statutory approvals of the installation from competent authority like Electrical Inspectorate, CEA, DGMS, SEB etc. including carrying out of all required modifications in design / Manufacturer / Installation to meet the requirement of Indian Electricity rules and other statutory regulations in force, carrying out necessary paper work and liasion with the authorities to obtain all necessary clearances for charging of installation as per relevant national standards for CNG stations. However the official fees towards the approvals shall be reimbursed by the client. | L/S | 12
A | TOTAL AMOUNT EXCLUDING GST
B | Applicable rate of GST (CGST&SGST/ UTGST or IGST) in % (in Column F of Excel sheet) applicable on the Total Amount mentioned at Sl. No. A above and GST Amount (in Column G of Excel sheet) Refer Note 1) below. |  |  |  | 18%
C | Gross Total Amount (inclusive of all applicable taxes & duties incl. GST) (Sl. No. A + B )
D | Service Accounting Code (SAC) Refer Note 2) below. |  |  |  |  | 995414
Notes: 1) Rate of GST indicated against sl. no. B above is the rate in general applicable on similar nature of work. Bidder must ascertain applicability of tax and it's percentage while submiting the bid. Any errors of interpretation of applicability of taxes/ duties by Bidders shall be to their account. 2) Service Accounting Codes (SAC) indicated against sl. no. D above is the code in general applicable for similar nature of work. Bidder must ascertain correctnes of the same while submiting the bid. Any errors of the same by Bidders shall be to their account. 3) In case of any item(s) provided by owner as free issue, the implication of GST on free issue items, if applicable, shall be borne by owner.
Place |  |  |  | BIDDER'S SIGNATURE:
Date |  |  |  | COMPANY'S NAME:
Tender No.: |  |  |  | SEAL:
Offer No. & Date :